{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":52,"n_cols":14,"rows_kept":52,"merged":[[0,0,0,13],[1,0,1,13],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,12,4,12],[2,13,4,13]],"flags":["formulas_cached_only"]}
["10上半月管网水半月检常规项目检验汇总表"]
["委托单位名称：淄博市自来水有限责任公司                                                                               检测单位：淄博安瑞水质检测有限责任公司                                                                                                                                                                                                                                                                                               "]
["序号","采样日期","采样地点","样品编号","菌落总数","总大肠菌群","色度","浑浊度","臭和味","肉眼可见物","二氧化氯","高锰酸盐指数（以O2计）","报告日期","检测人员"]
[{"$nulls":4},"CFU/mL","CFU/100mL","度","NTU","/","/","mg/L","mg/L"]
[{"$nulls":4},"≤100","不应检出","≤15","≤1","无异臭、异味","无","出厂水和末梢水中限值0.8，出厂水中余量≥0.1，末梢水中余量 ≥0.02","≤3"]
[1,"2025.10.09","新村西路140号原市水资办","20251009-0829",15,"未检出","<5","0.33","无","无",0.03,"/","2025.10.11"," 王晓芳"]
[2,"2025.10.09","淄博市政务中心","20251009-0830",17,"未检出","<5","0.35","无","无",0.04,"/","2025.10.11"," 王晓芳"]
[3,"2025.10.09","张店区疾控中心","20251009-0831",35,"未检出","<5","0.30","无","无",0.04,"/","2025.10.11"," 王晓芳"]
[4,"2025.10.09","西苑社区","20251009-0832",11,"未检出","<5","0.29","无","无",0.03,"/","2025.10.11"," 王晓芳"]
[5,"2025.10.09","五公里党群站","20251009-0833",38,"未检出","<5","0.22","无","无",0.05,1.35,"2025.10.11"," 王晓芳"]
[6,"2025.10.09","   市自来水公司南定营销服务中心","20251009-0834",22,"未检出","<5","0.33","无","无",0.04,1.17,"2025.10.11"," 王晓芳"]
[7,"2025.10.09","市自来水公司铝城营业所","20251009-0835",31,"未检出","<5","0.35","无","无",0.03,"/","2025.10.11"," 王晓芳"]
[8,"2025.10.09","经开区后南定村卫生室","20251009-0836",7,"未检出","<5","0.31","无","无",0.03,"/","2025.10.11"," 王晓芳"]
[9,"2025.10.09","张南路101号中石油加油站","20251009-0837",1,"未检出","<5","0.19","无","无",0.04,"/","2025.10.11"," 王晓芳"]
[10,"2025.10.09","山泉路启星比亚迪4S店","20251009-0838",5,"未检出","<5","0.30","无","无",0.05,"/","2025.10.11"," 王晓芳"]
[11,"2025.10.13","天勤苑社区","20251013-0839",14,"未检出","<5","0.27","无","无",0.04,1.24,"2025.10.15"," 王晓芳"]
[12,"2025.10.13","高新区金晶大道汇驰奔驰4S店","20251013-0840",2,"未检出","<5","0.22","无","无",0.03,"/","2025.10.15"," 王晓芳"]
[13,"2025.10.13","金都花园社区","20251013-0841",2,"未检出","<5","0.20","无","无",0.04,1.29,"2025.10.15"," 王晓芳"]
[14,"2025.10.13","星悦城社区","20251013-0842",10,"未检出","<5","0.21","无","无",0.03,1.26,"2025.10.15"," 王晓芳"]
[15,"2025.10.13","外商居住区","20251013-0843","未检出","未检出","<5","0.22","无","无",0.04,"/","2025.10.15"," 王晓芳"]
[16,"2025.10.13","市自来水开发区营业所","20251013-0844",3,"未检出","<5","0.17","无","无",0.05,"/","2025.10.15"," 王晓芳"]
[17,"2025.10.13","淄博市十一中","20251013-0845",8,"未检出","<5","0.27","无","无",0.03,"/","2025.10.15"," 王晓芳"]
[18,"2025.10.13","丽莎会议中心","20251013-0846",33,"未检出","<5","0.23","无","无",0.04,"/","2025.10.15"," 王晓芳"]
[19,"2025.10.13","华侨城警务室","20251013-0847",3,"未检出","<5","0.37","无","无",0.05,"/","2025.10.15"," 王晓芳"]
[20,"2025.10.14","淄博市委","20251014-0848",2,"未检出","<5","0.32","无","无",0.05,"/","2025.10.16"," 王晓芳"]
[21,"2025.10.14","张店区军休所","20251014-0849",7,"未检出","<5","0.33","无","无",0.04,"/","2025.10.16"," 王晓芳"]
[22,"2025.10.14","五里桥生活区","20251014-0850",5,"未检出","<5","0.20","无","无",0.03,"/","2025.10.16"," 王晓芳"]
[23,"2025.10.14","祥瑞花园社区","20251014-0851",22,"未检出","<5","0.17","无","无",0.04,"/","2025.10.16"," 王晓芳"]
[24,"2025.10.14","张店八中","20251014-0852",8,"未检出","<5","0.19","无","无",0.04,"/","2025.10.16"," 王晓芳"]
[25,"2025.10.14","淄博市图书馆","20251014-0853",10,"未检出","<5",0.33,"无","无",0.03,"/","2025.10.16"," 王晓芳"]
[26,"2025.10.14","积家村党群服务中心","20251014-0854",2,"未检出","<5","0.31","无","无",0.04,1.26,"2025.10.16"," 王晓芳"]
[27,"2025.10.14","明德苑社区","20251014-0855",9,"未检出","<5","0.20","无","无",0.03,"/","2025.10.16"," 王晓芳"]
[28,"2025.10.15","恒嘉园社区","20251015-0856","未检出","未检出","<5","0.27","无","无",0.04,"/","2025.10.17"," 王晓芳"]
[29,"2025.10.15","人民东路小学","20251015-0857",10,"未检出","<5","0.32","无","无",0.05,"/","2025.10.17"," 王晓芳"]
[30,"2025.10.15","张店区保安公司","20251015-0858",1,"未检出","<5","0.21","无","无",0.03,"/","2025.10.17"," 王晓芳"]
[31,"2025.10.15","润德实业公司","20251015-0859","未检出","未检出","<5","0.29","无","无",0.05,"/","2025.10.17"," 王晓芳"]
[32,"2025.10.15","行政执法局湖田中队","20251015-0860",11,"未检出","<5","0.28","无","无",0.04,"/","2025.10.17"," 王晓芳"]
[33,"2025.10.15","淄博市公交东站","20251015-0861",2,"未检出","<5","0.22","无","无",0.03,"/","2025.10.17"," 王晓芳"]
[34,"2025.10.15","洪三社区","20251015-0862",6,"未检出","<5","0.33","无","无",0.05,1.32,"2025.10.17"," 王晓芳"]
[35,"2025.10.16","淄博市工商局","20251016-0863",10,"未检出","<5","0.32","无","无",0.03,"/","2025.10.18"," 王晓芳"]
[36,"2025.10.16","市自来水公司新区营业所","20251016-0864",22,"未检出","<5","0.20","无","无",0.04,"/","2025.10.18"," 王晓芳"]
[37,"2025.10.16","颐臻园社区","20251016-0865",5,"未检出","<5","0.22","无","无",0.05,"/","2025.10.18"," 王晓芳"]
[38,"2025.10.16","世纪花园社区","20251016-0866",2,"未检出","<5","0.28","无","无",0.03,"/","2025.10.18"," 王晓芳"]
[39,"2025.10.16","瑞丰苑社区","20251016-0867",5,"未检出","<5","0.29","无","无",0.03,1.24,"2025.10.18"," 王晓芳"]
[40,"2025.10.16","科技苑物业","20251016-0868",9,"未检出","<5","0.33","无","无",0.04,"/","2025.10.18"," 王晓芳"]
[41,"2025.10.20","淄博市体育馆","20251020-0869",5,"未检出","<5","0.25","无","无",0.04,"/","2025.10.22"," 王晓芳"]
[42,"2025.10.20","福源汇社区","20251020-0870",1,"未检出","<5","0.33","无","无",0.05,"/","2025.10.22"," 王晓芳"]
[43,"2025.10.20","孝妇河湿地公园喷泉广场","20251020-0871",4,"未检出","<5","0.30","无","无",0.03,1.31,"2025.10.22"," 王晓芳"]
[44,"2025.10.20","石家社区","20251020-0872",8,"未检出","<5","0.29","无","无",0.03,1.23,"2025.10.22"," 王晓芳"]
[45,"2025.10.20","盛世康城社区","20251020-0873",3,"未检出","<5","0.30","无","无",0.03,"/","2025.10.22"," 王晓芳"]
[46,"2025.10.20","福瑞家园社区","20251020-0874",6,"未检出","<5","0.27","无","无",0.04,1.28,"2025.10.22"," 王晓芳"]
[null,null,"以下空白"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}